## TOC
Table of Contents for ALERT Protocols/Checklists
Internal working version, October 17, 2003
Tab | Link | Content | Internal Notes
Site |  | Basic site information. | Original ALERT material.
Renewables | Bldg | Screening questions for renewable energy opportunities. | Original ALERT material.
Bldg | Bldg | Basic building information. | Original ALERT material.
Inventory | Inventory | HVAC inventory overview. | Original ALERT material plus Before & After columns.
General | General | General schedules and other info. | Original ALERT material plus a few updates
AHU | AHU | Air handler and economizer checks. | Orig. ALERT checks plus new checks; reformatted for Before and After retuning work.
RTU | RTU | Rooftop unit diagnostic tool - Honeywell/Rossi handtool. | New topic area.
Boiler Q | Boiler Q | Boiler and distribution data to collect. | Orig. ALERT inteview questions plus many new questions.
Boiler | Boiler | Boiler and distribution checks. | Orig. ALERT checks plus many new checks.
Boiler Notes | Boiler Notes | Boiler and distribution notes and tips. | New 'rules of thumb' and low-cost action suggestions.
Air | Air | Compressed air data and checks. | New topic area.
IR | IR | Infrared camera tool checklist. | Orig. ALERT checklist.
Misc | Misc | Miscellaneous checks and suggestions for site staff. | Orig. ALERT checklist/suggestions.
Agenda |  | Generic agenda for site visit kickoff meetings.
Tools | Tools | Tool list for site visits - under construction. | Informal ALERT checklist used at PNNL with many new items added.
Notes | notes | In-progress development notes. | Casual, internal notes.

## Site
Basic Site Information
Adapted from the Part III ALERT Interview Record revised by J. Kelley, ~August 2003
1. Develop a breakout list of utility use and rates for at least gas and electricity.
Annual Consumption for Buildings to be Assessed
| Site Annual Consumption |  | Blended Rate
Natural gas |  | Therms or other | 0
Electricity |  | kWh
Water |  | Gallons
Sewer
Other
2. Gather monthly electricity and gas data for a 12 month period as appropriate.
3. What weather data is available? Prefer hourly dry-bulb temperature for the Typical Meteorlogical Year or Representative Year Data.
4. What site programs and end uses are essential or critical to maintain in the event of outages?
5. Do you recharge any utility costs to the occupant programs? What is the recharge method?
6. How much of the site's or buildings' electrical load can your generators provide? Can you provide basic information on the generators, including fuel, capacity, age, and ability to generate for long hours?
7. What capital or expense projects have been done, are underway, and are planned for the selected buildings?
8. What are operating hours for the site and/or common building types?
9. Please provide the following:
A. Site map with buildings and utility lines.
B. 1-Line diagrams of building floor plans.
C. Mechanical plans.

## Renewables
Renewable Energy Assessment Review
Adapted from the Part III ALERT Interview Record revised by J. Kelley, ~August 2003
Solar Hot Water
What facilities use a significant amount of hot water? Examples: dormitories, barracks, prisons, cafeteria, gymnasiums, swimming pools.
Building & HW Use | Amount of Hot Water* | HW Temperature | HW Heating Fuel | Cold Water Supply Temperature | Does facility have unshaded, south-facing flat/sloped roof or open ground for solar collectors? How close is it to the hot water use?
Ventilation Preheating
1. What are the requirements for ventilation air such as for process loads, airplane hangars, or chemical storage?
2. For ventilation requirements larger than 20,000 cfm: what are the cfm requirements?
3. How much wall space faces south, is free of doors and windows, and unshaded?
Photovoltaic and Wind Power
1. What are the small and remote electrical loads? Examples: remote monitoring stations, irrigation valves, and signboard lighting.
2. What are the kW and kWh/day requirements for these loads?
3. What site or building loads need a very reliable power? What are those uses and the amount of power needed?
4. What south-facing roofs near the power use have electrical service on or near the roof?

## Bldg
Information on the Building and HVAC system (previous Interview templates should have much of this info already.)
Buildings address:
Point of Contact for Building:
Phone number:
e-mail:
Total floor space of building and types of space:
Description of Building automation system:
BAS vendor: ______________ Name of Software:
Version of software:
Weather at start of inspection. Temperature _____, Wind _____, Humidity _____, Raining _____
Comments:
Weather at end of inspection if different. Temperature _____, Wind _____, Humidity _____, Raining _____
Comments:
Types of heating and cooling system used. Packaged heat pumps, central heating, central cooling, local heat cooling plant in building, all electric, etc. (If detailed data is available, then input it on the subsequent pages that call for more details.) :

## Inventory
HVAC Inventory (Sites may have an existing inventory to provide the ALERT team)
Heating System Type: ___________________________
Packaged Heating Systems? | Built-up Heating Systems? (The boiler tabs have more detailed questions)
No. of Systems: | No: of Boilers
Make and Size of Systems | Make and Size of Boilers
Economizer or Stack Reclaim
Are systems on networked (Y/N)
Cooling System Type: _______________________
Packaged Cooling Systems? | Built-up cooling systems?
No. of Systems | No. of Chillers
Make and Size of Systems | Make and Size of chillers:
Are systems on networked (Y/N)
Air handler systems: ______________________________ Cooling only:_________ Cooling and Heating: ________
Packaged System | Built-up System
No. of Systems: | No: of Chillers
Make and Size of Systems | Make and Size of Chillers
Economizer control: | No of AHU, and the CFM or HP of AHU
Are systems networked (Y/N) | Economizer control:

## General
Site-Wide and Building-Wide Interview & Field Checklist
Scheduling |  | Building# ______________
Checking activity | Before-Retuning Conditions | After
General Occupancy
What is the schedule? Do systems actually shut off during non-use hours? | Weekdays?: Weekends?: Shut off?: | Weekdays?: Weekends?: Shut off?:
What is the optimal start/stop, and does it work or is there a reset schedule? Do systems start early to warm up the building before staff arrive? If set for worst case winter condition, most of the time the building will be warm long before staff arrive. Use a reset schedule. | Start?: Stop?: | Start?: Stop?:
Janitorial: What is the schedule? | Weekdays?: Weekends?: | Weekdays?: Weekends?:
Is too much lighting and equipment running for a small number of staff in building? | Amount of lighting/equipment?: | Amount of lighting/equipment?:
Special Consideratons for Peak Load Periods
Can occupants tolerate resetting zone temperatures lower during peak times? | Yes/No/Maybe?: Existing practice and policy? | Controls programmed accordingly?:
Can occupants tolerate cycling air handlers off for 30 minutes at a time? (or at least turning off the cooling). | Yes/No/Maybe?: Existing practice and policy? | Controls programmed accordingly?:
Can occupants tolerate pre-cooling strategies (extra cooling at night and, therefore, cooler in the office in the morning). | Yes/No/Maybe?: Existing practice and policy? | Controls programmed accordingly?:
Fan and AHU
What is the ventilation schedule? | Weekdays?: Weekends?: | Weekdays?: Weekends?:
Supply, return, and exhaust fans? | Weekdays?: Weekends?: | Weekdays?: Weekends?:
Are schedules aligned with the occupancy schedules? | Yes/No?: | Yes/No?:
Plant
What is the heating/cooling plant schedule? | Weekdays?: Weekends?: | Weekdays?: Weekends?:
Can the plant be shutdown or idled during none working hours? | Yes/No/Maybe?: | Yes/No/Maybe?:
Are plant schedules aligned with the occupancy schedules? | Yes/No?: | Yes/No?:
Can the temperatures float in early evening? | Yes/No/Maybe?: | Yes/No/Maybe?:
Lighting
What is the lighting schedule? | Weekdays?: Weekends?: | Weekdays?: Weekends?:
Are lighting schedules aligned with the occupancy schedules? | Yes/No?: | Yes/No?:

## AHU
AHU Field Retuning Checklist
Review previous notes and diagnostic data (EMCS, WBD). Follow and fill-out checklists.
Building# ______________ AHU#: ___________
Checking activity | Before-Retuning Conditions | After-Retuning Conditions or Follow-up
Economizer
Check to see that the economizer section is running at minimum fresh air settings.
Override BAS to minimum ODA. | Position?: | Position?:
1. Override ODA temp to high value
2. Override ODA damper setting to minimum
3. Damper position per BAS?:
4. If dampers moved, what is their new position? | Position?: | Position?:
What is switch-over temperature? | Temperature?: | Temperature?:
Is economizer active during warm-up? It should be off or closed during morning warm-up before staff arrives to work. | Yes/No?: | Yes/No?:
Take the air temperatures to verify minimum mixed air. Check mixed air fraction by using temperatures of return, mixed and ODA. The Fraction = Mix-Rtn/ODA-Rtn. If above 10%, it’s getting too much ODA. Lower minimum position. Note: mixed air temperature set point does not play a part at this mode of operations so would not need to be checked unless mixed air temperature is below 40 degrees. Then limiting may be in effect.
| What is the minimum position?: | What is the minimum position?:
If ODA temperature is below 65, then is economizer running in economizer mode? | ODA temperature?: Economizer running?: | ODA temperature?: Economizer running?:
Check to see if dampers are modulating at mixed or leaving air set points or stuck. | Dampers modulating or stuck? | Dampers modulating or stuck?
If fan is on a variable speed or frequency motor, note the motor command (the % speed). | Command? | Command?
Is economizer active when building is unoccupied? | Yes/No?: | Yes/No?:
Check filters, the dirtier the more fan power is required to pull air through them. | Filter conditions? | Filter conditions?
Pressure is a cubed function on power. Normally runs less then ½ inch on larger clean filter systems. Good standard: Dp = 0.5” | Pressure with and w/o filter? | Pressure with and w/o filter?
Check cooling and heating coils for clean air side passage. If plugged or dirty causes a 2 fold effect. Higher pressure losses and less heat transfer. A 47 degree chilled water coil inlet temperature should get you a less then 60 degree discharge air temp from the coil. | Coil conditions? | Coil conditions?
Check cooling and heating valves for leakage by touching the piping inlet to the coil. If cooler then room or warmer then valve is leaking through. Touch leaving piping if there is a serious valve leakage problem and you should valve out the coil. You may need to valve out the effected coil until peak season is over. Primary concern is heating and cooling at same time. | Valves leaking? Heating lockouts? | Valves leaking? Heating lockouts?
Check cooling valve if 3-way is fully closed on the bypass side when in full-cooling mode. Normally this is done by checking temperature of bypass loop and looking at valve steam position. Check heating valve is system is in heating mode. | Closed? | Closed?
Dual Duct or Dual Deck: Is heating section fully off and cool? Check position of dampers and you will get an idea of the zone cooling needs. If most or all zones are calling for full cooling then you need to walk down some zones to see at what temperature they are running. Basically looking for zone that are heating or cooling more then required due to bad dampers or controls at the zone. | Total number of zones?: Zones not at set points?: | Total number of zones?: Zones not at set points?:
Discharge Air Checks
Check fan speed for running at 100% of speed or of vortex dampers position. If at 100%, then it may be working to hard. | Fan speed?: | Fan speed?:
Check discharge pressure. If above 1.5 inches ask yourself why. Do we really need this much pressure? If at 3 to 4” then you probably are too high. Try a lower setting and see what areas start to complain and why.A18 | Discharge pressure?: | Discharge pressure?:
Check discharge temperature. Can be from 45F to 100F. | Discharge air temperature?: | Discharge air temperature?:
Good standard range: >55F to < 70F.
If below 60, then it may be too low. Extra heat may be added that is not required. Air only needs to be cool enough to cool the warmest areas served. Ask if staff complain of sore necks or cold drafts. Do people have paper over the diffuser to direct the air away from them? This is a sign of too cold of air and maybe low flows.
If discharge temps are above 65F and chillers or cooling is operational discharge may be too warm and could use to be lowered.
Is discharge temperature too high or low for Outdoor conditions causing heating and cooling at the same time or a building with too many zones not at set point? | ODA temperature?: Discharge seem correct?: | ODA temperature?: Discharge seem correct?:
Is there a reset schedule? What are the settings? | Yes/No?: Schedule: | Yes/No?: Schedule:
Does the reset schedule match building’s true needs? Discharge temps are a critical balance point for the buildings current condition and thus can be changed to match building needs and minimize energy use. Recommend: design of reset algorithm for supply air temperature. | Fit with needs?: | Fit with needs?:
Return Air: Check balance and sequence of air flow in comparison to supply air and mixed air. Go through one economizer cycle and watch sequencing. | Observations? | Observations?
Generic Economizer Diagram
Outside Air Supply
Exhaust Air Opening
Return Air From Building
Supply Air Fan
Ductwork Dampers
Air Into Building
T
T
TT
Temperature Sensors
Controls

## RTU
Rooftop Unit Field Retuning Checklist - Mfr's instructions:

## Chiller
Chiller Field Retuning Checklists
Building# ______________ Chiller#: ___________
Checking activity | Before-Retuning Conditions | After-Retuning Conditions or Follow-up
If cooling system is running
How clean are condenser coils? | Clean?: | Clean?:
What is the physical condition of coils? | Condition?: | Condition?:
Air-cooled condensers saturation temps should be within 20 to max of 30 degrees of ODA temps. Water-cooled system should be within 10 to no more then 15 degrees. Centrifugals should be at about 10 degrees. All tower or condenser fans should be running above about 80 ODA.
Check condenser saturation pressure: | Pressure?: | Pressure?:
Derive condenser saturation temperature: | Temperature?: | Temperature?:
Determine approach = condenser saturation temperature minus ODA
Cooling sides and water chillers should be within 10 degrees of saturation temps or no lower the 40 degrees for DX style systems | Finding?: | Finding?:
Check water tower fill | Fill conditions?: | Fill conditions?:
Above 80F, ODA all tower fans should be running. | ODA at which all tower fans are running?: | ODA at which all tower fans are running?:
On centrifugal chillers: Check if at 100% FLA and if so is the vane operator still in a modulating mode. If fully open, chiller is probably under-charged. | Mode?: | Mode?:
Check chilled water temperature set point. Good standards/common-readings: 47 to 55F. Why is it down below 50? Can the system run at 47 or does it really require 42 and if so what is the true driver. This is the one setting that normally gets pushed down "just because".
Saturation pressure in evaporator: | Pressure?: | Pressure?:
Derive saturation temperature in evaporator: | Temperature?: | Temperature?:
Determine approach = Condenser Saturation Temperature minus Water Tower Exit:
Condenser water temperature set points should be as low as the machines can handle. 60 to 80F. The temperature maybe as low as 60 for some newer machines and 80 for older ones that have R-12 in them. | Temperature?: | Temperature?:
Water pumping systems: Check for bypass loops partially open bypassing some water. These should be closed anytime the system is at 50% or higher load. | Loops open?: | Loops open?:
If there are 3 way valves at the air handlers then they should not be used or not installed. | 3-way valves exist & used?: | Action?:
Check for more then 1 pump running on the same loop. Parallel pumping may not be required. | Pump configuration?: | Any action?:
Are we dehumidifying? Under 50% humidity may not be a realistic goal due to energy needs. | Reason for de-humification?: | Any action?:

## Boiler Q
Boiler and Distribution Systems Interview Checklist
Building# ______________ Boiler/System#: ___________
Point of Contact/Interviewee for Boiler: ___________________________________________________
Phone number: ________________________ | e-mail: __________________
No. of Boilers: | Utility Costs, Annual or Average Unit Cost (include units):
Mfg./Type Yr Built Rated Output(lb/h,psig) FuelType(#)[1] | 1. Natural gas _________________________
2. Fuel Oil ___________________________
3. Electricity __________________________
4. Compressed air ________________________
5. Other (i.e. water, with chemicals?)_________________
Auxiliary Equipment ( Y/N) include: steam separator, economizer, air-preheater heat exchanger (s) water softener: | Annual Utility Usage: (Consumables-include units):
Mfg./Type Date Built, Rated Output | 1. Natural gas ________________________
2. Fuel Oil __________________________
3. Electricity _________________________
4. Compressed air ________________________
5. Other (i.e. water, with chemicals?)________________
Do you use fuel switching to save $ (Y/N)
[1] List all fuel types that can be burned in the boiler, use numbers of cost structure section as applicable
Number of stack(s) for boiler(s) ________________ | Burner type/mfg.: (i.e. low Nox, Ring, steam/air atomized etc.)
Approximate height of the stack (s) | Nat.Gas: Atmospheric, ring, spud, low Nox
Draft design (Forced, Induced, Natural or Balanced) | Oil: Pressurize atomized, steam/air atomized,rotary cup
Coal: overthrow rotor chain, grate, windbox, pulverized
Intake location for draft fans (indication of temperature)
Boiler Control System Function: | Emission problems in the plant? (Y/N)
Maintain output of boiler (pressure or temperature) or Maintain combustion (i.e. air/fuel mixture)(O/C)? | Type of emission problems (Sox, Nox, particulates etc.)
Explain the type of System (i.e. lead-lag, O2 trim, etc.) | · How identified (monitoring?)
Networked System(s) (Y/N) | When was last time the burner was checked/tuned? (emission problems may indicate burner problems)
Boiler Demand Loads: Number, type and square footage of each building that receives steam/water from boiler plant? | What type of preventative maintenance program do you implement?
Audit of equipment, valves, control systems etc.
Boiler Demand Loads: Variable/Constant (V/C) | Calibration/repair of sensors, leaks, insulation
Describe daily/seasonal variations or variations over time (increasing/decreasing loads?) | Performance monitoring (including problem log (i.e. water hammer, widely varying boiler firing rate)
Boiler Blowdowns performed (Y/N) | Condensate return to boiler plant (Y/N)
Automatic, Manual or Continuous (A/ M/ C) ? | Quantify (annual, average or %, include proper units) _________________
Frequency of blowdowns (Hrly, Daily, as needed)____________ | Temp and/or source. of return water _________________
If condensate is returned is it polished? (Y/N)
How is the system controlled-to avoid excessive discharge? | If condensate is returned is it monitored for contamination? (Y/N)
Is there potential for heat recovery, blowdown energy or other?
Number/Type of steam traps _____________ | Feedwater make-up water source and temperature ___________
Steam traps audited (Y/ N) | Quantity of make-up water and how regulated? ___________
Frequency of audits (daily, qrtly, annually etc.)
Number/% operating properly? ______

## Boiler
Boiler and Distribution System Field Retuning Checklists
Building# ______________ Boiler/System#: ___________
Targets |  | Checking activity | Key | Current values, notes
Boiler Stack Gases |  | Check Combustion Efficiency at high fire with Bacharach: | goal >75% | 1. Temperature of stack gases ____°F
|  | Follow Bacharach recommended test procedures, and note location of test sample point (i.e. before or after induced draft fan, after damper, top of stack) Provide simple drawing. |  | 2. Ambient temperature ______°F
3. Percent oxygen in the stack ________%
4. Combustion efficiency reading ________ %
|  | Check Combustion Efficiency at low fire with Bacharach: | goal >60% | 1. Temperature of stack gases[1] ____ °F
|  | Follow Bacharach recommended test procedures, and note location of test sample point (i.e. before or after induced draft fan, after damper, top of stack Provide simple drawing. |  | 2. Ambient temperature ­____°F
3. Percent oxygen in the stack _____%
4. Combustion efficiency reading ________%
Feedwater Input, Fuel Input & |  | Check Thermal Efficiency at high fire by noting (This activity may not be feasible if time and/or instrument constraints exist): | overall goal >72% | 1. Temperature of feedwater ­­­____°F
Steam or Water Output |  | · If any other mass flow leaves or enters the boiler, the mass must be measured or eliminated (i.e. no blowdowns during the test run) |  | 2. Feedwater flow rate _____gpm
|  | · Direct measurements are preferred. | gas: 76-82% | 3. Steam/water (Temperature or pressure if water or saturated steam, if superheated steam, need both parameters) ____°F
|  | · Feedwater temperature can be taken at feedwater storage tank. | oil: 78-89% | 4. Fuel flow rate ­­­­____gpm
|  | · It may be possible to estimate feedwater flow by timing level increase in boiler drum | coal: 85-88%, note: varies w/load | 5. Fuel heating value (typically a constant-from utility/plant prior test.) ____ Btu/cu.ft., or Btu/gal
|  | · Note location of measured readings or where the readings came from if not directly measured. |  | For calculation sheet see Reference 1 Appendix. B & C [to be developed].
· Provide simple drawing.
Air System |  | Check Dampers: |  | Findings:
· The damper should move easily, show no signs of getting stuck open or closed, and follow the controls smoothly
· Look for wear or deformed linkage – lubrication?
Boiler |  | Check Burner Flame for: 1) Shape, 2) Color, 3) Uniformity |  | Findings:
· Want the shape to be uniform shape that matches the type of burner (i.e. a ring burner should have ring shape, if not part of burner may be plugged).
· The color indicates whether burning to rich or not. Good color would be Blue with yellow tips.
· Is the shape ragged at the edges or flickering up and down?
|  | Check Blowdown Controls: |  | Condition of valve/system (leaking?)____________
|  | · Check that the blowdown valve is not leaking by in the closed position. |  | Measure flow and temperature________
|  | · Manual or automatic blowdown should not be excessive. The blowdown need only be enough to eliminate solids from the blowdown boiler. |  | Quality of water/steam discharged (solids?)_________
· If a blowdown is performed by while you are testing, check the blowdown water for solids
Boiler |  | Check firebox temperature (exterior boiler walls) | <150F
Thermography may be used.
Boiler Drum |  | Check Water Level :
· Check that the water level in the boiler is not above high water mark or below low-level mark. Also, watch as boiler operates that the level is not fluctuating significantly.
· It may be possible to estimate feedwater flow or quantify amount of fluctuation of flwo by timing level increase in boiler drum.
Plant auxiliary equipment |  | Check vibration of aux. Equipment in the plant (i.e. fans, pumps etc):
|  | Check temperature of aux. Equipment in the plant (i.e. fans, pumps etc):
Thermography may be used.
Plant auxiliary equipment |  | Check current draw of aux. equipment
Look for hot equipment.
[1] A 1% efficiency gain for each 40F drop in temperature
Plant Aux. Eqpt. |  | Check Housekeeping items: Throughout the distribution system starting at the generation point.
1. Steam or water leaks and/or venting at the boiler or throughout the plant.
A. Measure temperature of the leak/venting.
B. Thermography may be used to measure temperature or trace back to the source to determine pressure and/or temperature.
2. Missing insulation (Typically if surface temperature is >120F, should consider insulation-especially for personnel protection)
A. Quantify by noting diameter, pressure and temperature of pipe as appropriate.
B. Note source/location in plant, and quantify energy loss if possible. Temperature of space, Thermography may be used.
3. Infiltration points into the boiler and controlled spaces (i.e. heated areas)
4. Equipment repairs needed, and/or clogged/stuck valves, and plugged heat exchangers.
Note source/location of above findings in plant, and quantify energy loss if possible.
|  | Check for steam use throughout the plant for possible substitution/modifications |  | Quantify by noting:
Diameter of pipe_________(pipe tape measure)
Steam tracing: Observe if steam tracing is used to reduce freezing in more than 15 places, it may be more economical to use a glycol solution.
|  | Check steam distribution-should be generated/transported at highest pressure (low specific volumes-smaller piping) but used at lowest pressure (higher latent heat available). |  | Pressure of pipe___________(locate source, and use)
Linear footage of heat traced pipe_________,
(standard tape measure)
Sketch of distribution layout with pressures and identifying source and users
Plant Aux. Eqpt. |  | Check for heat recovery opportunities |  | Thermography may be used to measure temperature of hot medium
Look for any sources of heat going to the sewer or air. (Note if can be determined, the chemical composition or source of the hot medium that is being dumped to the sewer or air
May be able to time amount filling a known volume
Measure temperature_________(thermometer)
Flow _______ May be able to time amount filling a known volume
|  | Check steam traps in the plant: |  | Note the type of trap used at the location
|  | If steam is in the pipe, a small stream may be okay, but a large stream of steam leaving the trap is typically a malfunctioning trap. |  | Note the medium that the trap is working on
|  | Take temperature upstream and downstream of the trap |  | (i.e. condensate or steam at a given pressure, if known)
|  | Location of traps (ie.ABCs, accessible, below drip points-low pts, close as possible to drip pt) |  | Ultrasonic trap tester(listening device)/ level meter (conductivity) and sightglasses *vaposcopes) may also be used to check whether the trap is working
|  | Check feed and boiler water |  | Water kits can be used (ph, hardness,)
|  | Check the water at several points throughout the feed water system. |  | Total dissolved solids (TDS) test strip kits and/or conductivity meter
Check the make-up water that enters the system.
Check a boiler water sample. Traces of chemicals used in the treatment or brought in with the make-up water should be identified. (If necessary, a sample may have to be analyzed at a lab)
REFERENCES:
1. Boiler Efficiency Improvement
2. CEM Training Course section P
3. O&M Best Practices Guide[1]
[1] Developed by PNNL, December 2002
Boiler diagram from T. Koehler, 8/4/03.
The quantity of sensors is idealistic; the ALERT process may not provide enough time to check all the points.
Feedwater
Control Valve
Steam
Outlet
BOILER
Steam
Separator
Separator
Return
Exhaust (stack)
Damper
Condensate
Tank
Feed
Pump
Control
Feedback
P
P
LT
T
P
P
F
LT
F
F
T
O
2
O
2
P
T
P
T
T
ambient
BOP
STACK
F
Make
-
up
water
Cond
.
Return
F
#2 fuel
oil
Gas
Header
Reg
Tank
Levels
Boiler Draft
Inlet Damper
P
Fuel Inlet
Feedwater
Inlet
Feedwater Header
Steam Header
C
pH
F
oil
gas
*
*

## Boiler Notes
Rules of Thumb Related to Boiler Systems
Combustion efficiency
Natural gas: 76-83%
Oil: 78-89%
Coal: 85-88%
- A 1% efficiency gain for each 40F drop in Temp
Insulation
- Typically if surface temperature is >120F should consider insulation-especially for personnel protection)
- 90% of the heat loss from a hot uninsulated surface can be economically eliminated by installing insulation.
Steam Traps
ABC’s of installation:
· Accessible for inspection and repair
· Below drip points
· Close to drip point
5% failure rate is considered a good target
Compressed air
- Every 2 psig increase in operating pressure requires an additional 1% in operating energy costs.
- Roughly 20 hp per 100 cfm at 100 psi
- Use outside air whenever possible, is generally cooler and denser-thus easier to compress
- Typically operate a: Reciprocating units, 1-50 Hp 100+ usually rotary or cenftugal

## Air
Air Compressor Interviewing & Retuning Checklists
Building# ______________ Compressor ID#: ___________
Interview Questions For Compressor Systems
Compressed air audited? (Y/ N)
What type of compressor(s) ?
Frequency of audits (daily, qrtly, annually etc.)
Do you operate at full load (Y/ N) ?
What are the loads?
Can pressures be reduced? (Y/ N)
Field Checks for compressor systems
Targets |  | Checking activity | Current values, notes
Compressed Air System |  | Air compressor operating pressures (Every 2 psig increase in operating pressure requires an additional 1% in operating energy costs) | Pressure
|  | Air compressor intake temperature, (should be from the coldest location feasible) | Settings. ______________________
|  | Air compressor intake source | Location within building (note distance to outside)______________________
|  | Throughout the plant you may find (be able to hear) compressed air leaks. These may be easy to hear and trace back to the source. | Diameter of pipe_________
Pressure of pipe________
Temperature of pipe_________
|  | Operating point of compressor (electrical consumption) | Compressor motor nameplate (bhp)__________
Motor nameplate efficiency_________
Motor logger (hours of operation)

## IR
Infrared Survey Checklist
The following IR protocol assumes the individual performing the IR survey activity is knowledgeable of this technology to a level commensurate with recommendations by ANST for Level I certification.
IR survey opportunities and needs will change depending on facility design. Use the following survey suggestions as applicable for site under examination. If IR anomaly found, fill out information as applicable using “IR Anomaly Data Sheet”, Addendum “A”.
Boilers |  | 1. Survey fire box for evidence of refractory deterioration. | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
2. Survey boiler for evidence of air inleakage or exhaust.
3. Survey blowdown lines, relief valves, drain isolations and other possible system penetrations for evidence of improper heat loss/leakage.
Steam Systems |  | 1. Survey system drains/blowdown lines for system heat loss. | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
2. Survey system steam traps for proper operation and evidence of excessive heat loss (ensure proper trap operation).
3. Survey System lines for evidence of inadequate insulation
Hot |  | 1. Survey heat exchangers for proper operation and validation of installed instrumentation. | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
Water
Systems
Pumps |  | 1. Survey for indication of alignment problems. | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
/Motors |  | 2. Survey for indication of bearing overheating
3. Survey for indication of motor overheating
Building |  | 1. Survey for evidence of air loss/inadequate insulation. | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
Envelope |  | 2. Survey roof if time of year and weather conditions conducive to survey needs, i.e. dry roof, clear sky, evening hours.
Misc. |  | 1. Survey radiant floor heating for evidence of coil leakage/blockage | If anomaly found, complete information as defined on “IR Anomaly Data Sheet”, Addendum “A”
2. Survey heating and cooling coils at VAV boxes and similar system heat exchangers for evidence of simultaneous heating and cooling..

## Misc
Suggestions Checklist
General Suggestions for Sites
Cooling
Never run 2 chillers at part load when one machine can carry it even if the chilled water temp slips a little.
Hot Water
Put a timer on all electric hot water tanks and turn them off during all the peak time windows. Storage can normally carry you through.
Lighting
Turn off hall lights. Take every second light bulb out of fixture.
Turn off parking lot lights away form the building and have people move their cars closer who are working late.
Have lights been retrofitted to commercial best efficiency? (example:T8s and electronic ballasts)
Users
Always turn off computers when not in use.
Check if all of the staff’s lunch refrigerators are being used. Unplug those that are lightly used and consolidate.
Put timer on office water coolers. Generally, there is significant storage to carry sufficient cold water through major portion of the peak period.
Allow for alternate work schedules with additional shift to reduce operations during the day’s peak period (usually mid-afternoon). Instead of, say, 9am – 5pm suggest 2 shifts, say, early day (6 am to 2:30 pm) and late day (after 5 pm).

## Tools
|  |  | Tools Checklist |  | Trip: ____________
|  |  | Ck | Auditing Equipment | Action
Item # | Priority 1=high, 2=med.3=low | redundancy check | Ck | Auditing |  | How used?
1 | 1 |  |  | Infrared (IR) Gun - surface temperature measurement (take mat-black tape to get good emmissivity) | Darrel Hatley | equipment hot spot detection
2 | 1 |  |  | Thermocouple or RTD Thermometer with various probes suitable for surface and air stream direct measurement | Solomat, resides in room storage rm #1414,Needs calibration | effiiciency, heat recovery potential, check actual vs.design condition-reset opportunity
3 | 2 |  |  | Light Meter - light level readings | Eric Richman | check actual vs. design condition, comfort level
4 | 2 (3) |  |  | Watt Meter - simple power demand and consumption measurement |  | check actual vs. design condition, efficiency
5 | 3 |  |  | Tachometer-measure rotational speed of equipment, such as motors, fans (rpm) | Solomat has attachment probe, we do not own
6 | 1 | same as 15&16? |  | Single channel HOBO Temperature and Humidity Data loggers without external input capability | John Hail has pack
7 | 1 |  |  | Duel Channel Hobo data Temperature and Humidity Data Loggers with duel external input capability. (x3) | Need to purchase
8 | 1 |  |  | Hobo H6 Motor logger On/off data loggers (x3) | Need to purchase
9 |  |  |  | Data logger external input sensors: | Need to purchase
10 | 2 |  |  | 20 amp CT split core (x1) | Need to purchase
11 | 2 |  |  | 50 amp CT split core (x1) | Need to purchase
12 | 2 |  |  | 100 amp CT split core (x1) | Need to purchase
13 | 1 |  |  | temp. sensor with 6 ft. cable (x2) | Need to purchase
14 | 1 |  |  | temp. sensor with 20 ft. cable (x2) | Need to purchase
15 | 3 |  |  | Ballast Detector - magnetic or electronic
16 | 3 |  |  | Window Coating Detector -indicates low-e coating on which surface
17
18 | 3 |  |  | Pressure gauge-to install in existing taps
19 | 2 |  |  | D/P measuring device (like magnehelic): for low differential pressure measurements, used with pitot static tubes.
20 | 1 |  |  | Infrared camera | Sue Arey
21 | 1 |  |  | Digital camera | Sue will get from Steve
22 | 1 |  |  | Bacharach-boiler combustion efficiency testing | Needs new 02 cell every 6 months or so. See Ray or Greg Sullivan. Also large unit in 2400 storage | indication of boiler operating condition & efficiency
23 | 2 |  |  | Water kit (Ph, hardness, total dissolved solids) | Solomat, resides in room storage rm #1414,Needs calibration | indication of boiler physical condition & efficiency
24 |  | same as item# 6&7? |  | Solomat data collector (for suite of Solomat sensors) | Solomat, resides in room storage rm #1414,Needs calibration
25 | 2 | same as item# 25? |  | Airspeed probe: Hotwire probe, with telescopic or gooseneck handle, suitable for measurements in ducts, registers or grilles. | Solomat, resides in room storage rm #1414,Needs calibration | effiiciency, heat recovery potential, check actual vs.design condition-reset opportunity
26 | 3 |  |  | Airspeed probe: Vane probe, with telescopic or gooseneck handle , designed for high speed/high accuracy measurements | Solomat, resides in room storage rm #1414,Needs calibration | same as above, different tip design
27 | 3 | same as item# 9? |  | Hygrometer probe: measures relative humidity (%RH), and contains PT100 temperature sensor, designed for fast response and quick spot checks or continuous monitoring, Duplicates current HOBO capability) | Solomat, resides in room storage rm #1414,Needs calibration-cost $175 per sensor, perhaps more for this sensor, takes 3 weeks to 1 month | effiiciency, heat recovery potential, check actual vs.design condition-reset opportunity
28 | 3 |  |  | Doppler (non-intrusive) flowmeter 0.03 to 12 m/s (0.1-40 ft/s) (with ultrasonic pipe thickness tester, metal file/sandpaper/metal brush, utility knife, allen wrench, couplant fluid) | Panametrics Transport model PT868 resides in room storage rm #1414 at least one unit is known to be calibrated | effiiciency, heat recovery potential, check actual vs.design condition-reset opportunity
29 | 10 | same as 32? |  | Bucket (volumetric container) and stop watch (measure flow) |  | back-up method to doppler-(see above)can use if line Is not full or turbulent flow-pipe runs are too short for Doppler
30 | 3 |  |  | Magnet (carbon vs stainless steel lines)-one set-up for doppler is magnets |  | may indicate source of meatl contamination, mettalurgy suitability for application
31 | 1 | same as 36? |  | Ultrasonic (sonic) gun/meter -check equipment for vibration, poor performance (i.e. steam traps) | Ray Pugh | Used to define bearing problems, steam trap leakage, air system leaks, underground water leaks, gas line leaks, etc.
32 |  |  |  | Vibration meter-check equipment for vibration problems (if generate heat may pick-up with thermal gun) |  | indication of equipment physical condition & efficiency
33 |  |  |  | Misc/Ea. Person
34 | 1 |  |  | Clipboard
35 | 1 |  |  | Paper tablet
36 | 2 |  |  | Highlighter
37 |  | same as 13&14? |  | Post-Its
38 |  |  |  | Flashlight
39 |  |  |  | Pipe diameter tape measure (Caliper would be better for diameter)
40 |  |  |  | DOE badge
41 |  |  |  | Standard tape measure
42 |  |  |  | Batteries/Extension cord for power supply needs
43 |  |  |  | Hard hat
44 |  |  |  | Safety glasses
45 |  |  |  | Safety shoes
46 |  |  |  | Ear plugs
47 |  |  |  | Tools, wrenches, screwdrivers, spanners, etc.
48 |  |  |  | Tool and equipment case (roller case good idea)
49 |  |  |  | Instrument calibrator(????)
50 |  |  |  | Other Items
55 |  |  |  | Building and HVAC inventories
Filled-out interview forms
Pre-analysed diagnostic results
|  |  |  | Laptop projector | Paul King
Powerpoint files
|  |  |  | Workshop binders or handouts | Deb Beattie
Copies of agenda

## Agenda
Blank rows to make Max Stop formula work well
ALERT Site Visit Agenda
site name | site name
date, location | date & location
hidden formulas
Date | Start | Stop | max Stop | Min. | Item |  | Lead
2003-10-28 | 9:00 | 9:30 | 9:30 | 30 | Kickoff the site visit
|  | … | 9:30 |  |  | Introduce players
|  | … | 9:30 |  |  | Review the purpose of the ALERT assessments | ALERT team leader
|  | … | 9:30
| 9:30 | 10:00 | 10:00 | 30 | Plan/Confirm the assessment schedule |  | ALERT team leader
|  | … | 10:00 |  |  | Review the building priorities
|  | … | 10:00 |  |  | Set approximate schedule for each building
|  | … | 10:00 |  |  | Confirm availability of site staff
|  | … | 10:00
| 10:00 | 10:30 | 10:30 | 30 | Brief tour/orientation of site & targeted buildings |  | Site leader
|  | … | 10:30
| 10:30 | 12:30 | 12:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 12:30
| 12:30 | 14:30 | 14:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 14:30
| 14:30 | 16:30 | 16:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 16:30
| 16:30 | 18:30 | 18:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 18:30
2003-10-29 | 8:00 | 8:30 | 8:30 | 30 | Reconvene |  | Team
|  | … | 8:30 |  |  | Review the building priorities
|  | … | 8:30 |  |  | Set approximate schedule for each building
|  | … | 8:30 |  |  | Confirm availability of site staff
|  | … | 8:30
| 8:30 | 10:30 | 10:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 10:30
| 10:30 | 12:30 | 12:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 12:30
| 12:30 | 14:30 | 14:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 14:30
| 14:30 | 16:30 | 16:30 | 120 | Assess bldg/system _________________________ |  | Team
|  | … | 16:30
| 16:30 | 17:00 | 17:00 | 30 | Debrief |  | ALERT team leader
|  | … | 17:00 |  | 15 | Review the general lessons-learned
|  | … | 17:00 |  | 15 | Review the remaining needed info an tasks
|  | … | 17:00
| 17:00 | 17:00 | 17:00 |  | Close
|  | … | 17:00
|  | … | 17:00

## notes
.
Add to Interview Questions
Where's the natural gas go on site?
If 5 bldgs/boilers, then make them priority
Where's the high pressure steam?
Renewables: check for methane potentials - water treatment plants; landfills.
Is "Take or Pay" asked in the Interview?
Protocol Improvements
units missing
add more motor checks?
add more pump checks?
screening for high priority bldgs/components.
O&M contract language improvemtns
Integrate O&M Best Practice Guide
Tablet PC approach for integration and data and calculations.

## Fraction
Mix | - Rtn | =
|  |  | ------------ | = | %
ODA | - Rtn | =

## Condenser
Determine approach = cond. Sat temp – ODA
| Condenser Sat. T. | =
| - Outdoor Air T. | =
| -------------------------------- | = | --------------------------------
| Approach | =
| Condenser Sat. T. | =
| - Water Tower Exit T. | =
| -------------------------------- | = | --------------------------------
| Approach | =

## HW
.
*Estimated hot water use
(Gallons/Day/Person)
| Dining | 20 | Prison | 34
| Dormitory | 34 | R&D | 7
| Hospital | 34 | School | 2
| Housing | 15 | Services | 2
| Industrial | 4 | Storage | 2
| Offices | 3 | Other | 3